*_41_TECH__POWER_FAILURE_AND_REBOOT_PROCESS*

*FORMATTING RULE FOR ALL APOLLO RESPONSES*

Links MUST always be embedded: <URL|Display Text>. Never paste a raw URL.

- *Bold* uses single asterisks. Never use **double asterisks**.

- Do NOT use [text](url) markdown link format. Always use <url|text> Slack format.

- Do NOT use # or ## headers in responses. Use *bold labels* instead.

- Bullet lists use - or *. Numbered lists use 1. 2. 3.

---

*Purpose*

This file defines how Apollo should answer questions about power failures, UPS and BPU devices, the Tripp Lite, and the correct bootup sequence to restore store functionality after a power outage.

*When to Use This File*

Use this file when the user asks about:

- what to do during a power failure,

- how to handle guests during a power outage,

- UPS, BPU, or Tripp Lite location or function,

- how to reboot after a power failure,

- the correct bootup order for Synology and BeeLink/N100 devices,

- SPC not booting after power is restored,

- confirming everything is working after a power event.

*When Not to Use This File*

Do not use this file for:

- routine server maintenance,

- vest or tracker power issues,

- HTC power cycling for non-outage reasons.

*Priority / Override Rules*

- Submit the T1 Slack Power Failure Report Workflow FIRST before rebooting anything. Do not skip this step.

- If internet is down and Slack is inaccessible, contact the Ops Leader or Franchise Operations Support Partner instead.

- If the power outage affects neighboring stores, contact the Ops Leader immediately.

- Bootup order and timing are critical. Do not skip steps or rush the wait times.

- Do not attempt the bootup process without first completing the guest handling steps and the Slack workflow.

*Handling Guests During a Power Failure*

The steps below are guidelines. Use best judgment for the specific situation.

1. Check on guests immediately. If guests are in an experience, approach them, remove their headsets, and calmly explain the situation. Example: "Hi everyone, it looks like we've had a power issue. You're safe, but we'll pause your experience while we work on getting everything back up."

2. Move guests to a safe, well-lit area. Guide them from the holodeck to the lobby or just outside the store. If in a mall or strip mall, ask guests to wait just outside for further instructions.

3. Update guests on next steps. Let them know you are assessing the situation and will update them within a few minutes.

4. Evaluate the situation. Determine whether power will be restored quickly (within 10 minutes) or if longer delays are expected. Consult the Ops Leader if problems persist.

5. Rescheduling and compensation. If the experience cannot continue: reschedule for a later time or date. Partner with the Ops Leader on goodwill gestures (discounts, free rebooking, water, snack boxes, refunds). Use Checkfront to reschedule or refund as appropriate.

6. Communicate with upcoming bookings. If the issue will impact upcoming bookings, proactively call guests scheduled within the next 2 hours. Inform them of the situation and offer to reschedule or refund.

Note: verify whether the power outage is limited to the Sandbox store or affects neighboring stores. If neighboring stores are also impacted, contact the Ops Leader promptly.

*UPS and BPU: What They Are and Where They Are*

*UPS (Universal / Uninterruptible Power Supply) -- also called Tripp Lite*

- Provides backup power for critical systems during an outage.

- Located at the base of server racks -- both Holodeck/Room server racks and backroom IT server racks, if the store has them.

- The front LCD displays INPUT voltage. A reading of 120V confirms the unit is powered. The display rotates through multiple screens -- wait for the INPUT VOLTS screen to confirm.

- Not all stores have a UPS. Stores without a UPS use a BPU Power Strip instead.

*BPU Power Strip*

- Rack-mounted. Located in IT Rack 1 and in each Holodeck Server Rack.

- Not the same as an APC. A server rack will have both a BPU and an APC.

- Trace the BPU power cable to its wall outlet to confirm the outlet has power.

*Tripp Lite*

- Tripp Lite is a brand of UPS (Universal/Uninterruptible Power Supply). Treat any Tripp Lite question the same as a UPS question.

- Located at the base of each server rack -- both Holodeck/Room racks and backroom racks -- if the store has them.

*UPS Reboot Process*

*If the store has NO UPS (Workflow A -- BPU stores)*

1. Check if neighboring stores have power to confirm whether this is a local outage.

2. Locate the BPU Power Strip and confirm it is powered on.

3. Trace the BPU Power Cable to its wall outlet and confirm the outlet has power.

4. If the outlet has power but the BPU does not, the BPU may need replacement. You can temporarily bypass it using a power strip.

5. If the outlet has no power while other nearby outlets do, the breaker may be tripped. Contact T2 Support.

*If the store HAS a UPS (Workflow B -- UPS/Tripp Lite stores)*

1. Check if the UPS has power. Look at the front LCD. Confirm INPUT reads 120V. Wait for the voltage screen -- the display rotates.

2. If the UPS has no power:

a. Locate the reset button on the back of the UPS and press it.

b. Press and hold the power button on the front of the UPS for 5 seconds.

c. If still no power, trace the UPS power cable to the wall outlet. Plug in another device (such as an iPad charger) to confirm the outlet has power.

3. Contact T1 on Slack using the Power Failure Report Workflow and fill out all questions.

4. If Slack is inaccessible due to internet outage, contact the Ops Leader or Franchise Operations Support Partner.

*Bootup Process (After Slack Workflow is Submitted)*

*Submit the T1 Slack workflow first. Do not reboot anything until this is done.*

Bootup order and timing are critical. Follow exactly.

*Before proceeding*

Verify that all devices have lost power and are off. Identify whether the UPS failure is in a Room Server Rack (at each holodeck) or in an IT Rack (backroom). This determines where you start:

- Room Server Rack: power on that room's servers.

- IT Rack (SPCs): check that SPCs on that rack are powered on.

- IT Rack containing Synology and BeeLink (N100/N150) devices: proceed with the full bootup sequence below.

*Step 1 -- Power on APC PDUs*

Press the reset button on the back of the APC PDU in both Holodeck and Backroom Server Racks. Then plug in the power for the APC PDU.

*Step 2 -- Power on Synology*

Power on the Synology. Wait at least 7 minutes before proceeding to the next step.

*Step 3 -- Power on BeeLink (N100/N150) #1*

Power on BeeLink #1. Wait at least 30 seconds before moving to the next step.

*Step 4 -- Power on remaining BeeLinks in order*

Power on BeeLink #2, then #3, then #4, with at least 30 seconds between each one.

*Step 5 -- Turn on SPCs*

Turn on the SPCs in both Holodeck and Backroom Server Racks.

If an SPC will not boot:

1. Confirm the APC is plugged in and has power.

2. Unplug the SPC.

3. Wait 30 seconds.

4. Plug it back in.

5. Press and hold the power button for 3 seconds.

6. If it still does not turn on, contact T1.

After completing this sequence, the network and WiFi should be restored. It may take several additional minutes for the WiFi prop gateway to come online.

*Final Confirmation Checklist*

After rebooting, manually confirm all of the following are powered on:

- Synology

- APC PDU

- BeeLinks (N100/N150 #1 through #4)

- Room Servers

- SPCs

- UPS or server rack power strips/surge protectors

- Recap TVs

- Barracks TVs

- Store Front TV

- Headsets (if applicable)

Then confirm functionality:

- Run test sessions in all affected rooms.

- Check HTC connection.

- Check prop gateway and verify props are responding.

- Confirm all iPads are connected to WiFi.

- Confirm reservations are showing in the waiver app on iPads.

If any of the above is not functioning as expected, contact T1.

*Required Oasis Link*

You can review this topic on the Oasis page below, which contains the related SOPs, eLearnings, and guides.

<https://sites.google.com/sandboxvr.com/theoasis/home/store-operations/guest-centric-operationally-sound/tech-sops-and-elearnings/power-failure|View Power Failure SOP on Oasis>

*Trigger Phrases*

- power failure

- power outage

- store lost power

- UPS

- BPU

- Tripp Lite

- TrippLite

- where is the UPS

- where is the Tripp Lite

- reboot after power failure

- Synology bootup

- BeeLink bootup

- N100 bootup

- SPC won't boot after outage

- bootup order

- power restore sequence

- backup power

- what powers the servers

*Exclusions*

- Do not reboot anything before submitting the T1 Slack Power Failure workflow.

- Do not skip or reorder the Synology/BeeLink bootup sequence.

- Do not rush wait times (7 minutes for Synology, 30 seconds between each BeeLink).

- Do not confuse BPU with APC -- a rack will have both.

- Do not say Tripp Lite is software or guest-accessible equipment.

*Example Response Patterns*

- "During a power failure, first check on guests and move them to a safe area, then determine whether to use Workflow A (BPU stores) or Workflow B (UPS stores) to restore power. Submit the T1 Slack Power Failure workflow before rebooting anything."

- "The Tripp Lite is a UPS (backup power unit). It is located at the base of each server rack -- both Holodeck/Room racks and backroom IT racks -- in stores that have them."

- "Bootup order after a power failure: APC PDU first, then Synology (wait 7 minutes), then BeeLink #1 (wait 30 seconds), then BeeLinks #2 through #4 in order (30 seconds between each), then SPCs."

- "Submit the T1 Slack Power Failure Report Workflow first. Do not reboot anything until that is done."